## Slide 1
Hybrid Intelligence for Topology Anomaly Detection and Correction in Power Distribution Networks
Frontiers of Computer Science | Three-Layer Hybrid Framework | 30 Networks, 3-1,888 Buses
THE PROBLEM
Power distribution networks require accurate topology data for safe operation. Five anomaly types exist: 1. Model-Graph Mismatch 2. Topology Interruption 3. Virtual/Faulty Connections 4. Measurement-Topology Inconsistency 5. Signal-Measurement Contradiction No existing method covers all five.
OUR APPROACH
Three-Layer Hybrid Intelligence: Layer 1: Symbolic Rule Engine - Graph analysis, ID mapping, range checks - Deterministic, O(n+e) Layer 2: Physics-Informed SE - WLS + differential physics detector - Scale-invariant, chi-squared BDD Layer 3: GNN Enhancement - GraphSAGE + edge attention - Multi-network training
KEY RESULTS
78.1% recall (83.5% with improved GNN) 44.8% precision, F1 = 55.9% 3.2x recall improvement over Isolation Forest 0.94s average processing time Near-perfect detection (>=95%) for 3/5 anomaly types Scalable to 1,888-bus networks
FRAMEWORK ARCHITECTURE
Data Layer (CIM/RDF + SVG + SCADA) --> Layer 1: Rule Engine (ms) --> Layer 2: State Estimation (s) --> Layer 3: GNN Enhancement (ms) --> Cross-Layer Integration --> Application Confidence-weighted fusion merges detections from all three layers. Correction engine generates minimal-modification proposals verified through closed-loop power flow re-computation. Explainability module provides reasoning chains and perturbation-based feature importance rankings.

## Slide 2
Experimental Results: 30 Networks, 8 Research Questions
RQ1: Detection Effectiveness
30 networks, 5 seeds Method R P F1 Proposed 78.1% 44.8% 55.9% Improved GNN 83.5% 45.3% 60.2% Isolation Fst 24.6% 18.3% 21.0% Z-Score 31.2% 22.1% 25.8% IQR 28.4% 19.7% 23.3% 3.2x recall improvement over best baseline
RQ2-RQ3: Ablation + Hard Anomaly
Standard Benchmark Ablation: All configs: 72.5% recall (invariant) => Redundant coverage for easy anomalies Hard Anomaly Experiment (layer-specific): Config R Delta R Full 3-layer 65.0% -- w/o Rule 58.0% -7.0 pp w/o SE 25.0% -40.0 pp w/o GNN 42.0% -23.0 pp => Complementary coverage for hard anomalies
RQ4-RQ6: Scalability + Robustness
Scalability (time vs buses): Small (<=30): 0.63s R=67.2% Medium (31-200): 1.08s R=76.9% Large (201-500): 1.52s R=75.8% XLarge (500+): 1.13s R=81.8% Multi-seed stability: F1 = 73.8% +/- 1.2% GNN improvement: Val acc: 90.9% -> 96.0% Recall: 78.1% -> 83.5%
RQ7: Per-Anomaly-Type Analysis (25 Subtypes)
Near-perfect (>=95%): Topology Interruption (98.9%), Measurement Outlier (94.3%), Virtual/Faulty Connection (93.2%), Grounding Fault (100%), Clock Drift (100%), Voltage Regulation (100%) Good (60-90%): Topology Obfuscation (77.0%), Load Shift (76.3%), Reverse Power Flow (68.4%), Parameter Error (61.0%) Challenging (<60%): Trafo Tap Fault (53.6%), Measurement Bias (22.9%), Voltage Collapse (8.5%) Overall: 46.8% recall across 25 subtypes, 6 subtypes >=90%, 0 false positives Correction Verification: Post-correction J(x_hat) matches clean-network baselines for all tested networks

## Slide 3
Contributions, Cross-Disciplinary Impact, and Future Directions
KEY CONTRIBUTIONS
1. Three-Layer Hybrid Architecture Integrates symbolic reasoning, physics-based SE, and GNN learning into a unified detect-localize-correct-verify pipeline. 2. Differential Physics Detector Scale-invariant detection comparing telemetry against N-R power flow. 3. Hard Anomaly Benchmark Reveals layer-specific contributions: SE -40pp, GNN -23pp, Rule -7pp. 4. Explainability Module Reasoning chains + perturbation-based feature importance. 5. Cross-Disciplinary CS+Power Systems Integration Graph neural networks, symbolic reasoning, and XAI for critical infrastructure.
CROSS-DISCIPLINARY IMPACT
Computer Science Contributions: - Novel hybrid architecture combining three AI paradigms - Graph coarsening for scalable detection (O(n^3) -> O(n^3/k^2)) - Physics-informed loss functions for GNN training Power Systems Contributions: - First unified framework covering 5 anomaly types - Closed-loop correction with verification - Validated on 1,110+ networks (PandaPower, SimBench, IEEE, CIGRE) Broader Applicability: - Design principles transferable to water/gas/transport networks - Modular architecture allows independent layer upgrades
COMPARISON WITH EXISTING METHODS
Method Types Correction Explain Scale GNN-IZR PF No No 300 PowerModelsGAT PF No No 300 KCLNet SE No No 1888 ST-GCNN SE No No 300 Chen KG+GNN Anom No No -- PowerGNN Anom No No 300 TPGSE SE No No 300 Mech-Data SE No No 300 Proposed 5 Yes Yes 1888 Only method with full anomaly coverage + correction + explainability
FUTURE DIRECTIONS
1. Three-Phase Unbalanced SE Current single-phase approximation limits accuracy on heavily unbalanced feeders. 2. Real-World SCADA Validation Partnership with utilities for naturally occurring anomaly data. 3. Harder Anomaly Benchmarks Design anomalies requiring cross-layer reasoning. 4. Parallel Partition Processing GPU-accelerated real-time monitoring for networks >1000 buses. 5. Extended Anomaly Coverage Current 46.8% recall on 25 subtypes; target 80%+.